Subsea DC Collection Grid with High Power Security for Offshore Renewables

D. Jovcic,     H. Zhang     D. Findlay     A.Z. Annuar      B. Li

Abstract-- This paper presents a subsea DC collection grid with renewable power parks which inherently has robust DC fault protection and flexible expansion capability. By virtue of the applied DC/DC converter and the proposed DJ-Index Clamping control, different sections of the subsea grid are functionally interconnected and in the meantime decoupled in the event of DC faults. The faults are selectively isolated without the need for fast DC circuit breakers and system recovery from the faulty DC intertie branch is achieved by a coordinated operation strategy on DC/DC converters and DC disconnectors (or standard AC circuit breakers). A 200MW test system is presented which consists of two 100MW renewable energy sources (tidal stream and wind) and DC collection/transmission grids. The simulation results confirm the N-1 security of the presented topology and good control performance over a range of DC faults.

Index Terms-- power system control, power system operation, power system protection, power system simulation, renewable energy integration, smart grid

# Introduction

Historically the absence of high DC voltage conversion techniques and fault isolation components hindered the wider use of DC for transmission. Today the meshed DC grid with a large number of converters has been envisaged as both economically and technically feasible, and subsea applications as such will potentially see its strong application in collecting sustainable power from offshore renewables, or in the interconnection of different electric transmission systems [1][2].

A power transmission/distribution system demands operation with a high level of reliability and especially for the subsea power systems the system protection schemes need to be critically evaluated. This is demonstrated with the Ocean Observatory projects like NEPTUNE and others [3][4], where the marine environment requires heavier capital investment while imposes difficulty in system accessibility, compared against land systems.

Fault transient study and management in DC grids is significantly more difficult compared with AC systems [1][5][6]. The low impedance with DC circuit will allow the fault current to rise fast and significantly without current zero crossings. Should the concept of DC circuit breaker still be applied on wider grid scale, the stringent requirements on DC grid security will require the fault currents to be interrupted in a few milliseconds, typically 2-5ms. This is an order of magnitude faster than in AC grids and in this case DC breakers will have to be located at the terminations of all transmission lines/cables to avoid grid-wide voltage collapse. DC CBs (Circuit Breakers) with such high performances may take 30% of VSC converter cost, and up to date such DC CBs are not commercially available [7].

Nowadays, wind energy generation technologies are mature, while the technologies for converting ocean powers are still in infancy. Due to inherent characteristics of ocean energy especially within the ocean wave category, a number of converter concepts are present, and it is expected that multiunit tidal current and ocean wave plants will constitute the norm of the future [8]. Their grid interconnection is complex and in many cases DC collection systems are preferred.

The DC/DC converters enable multiple functions in DC grids, and they can simultaneously perform as DC circuit breakers [9][10]. Under fault conditions, this DC/DC converter naturally restricts the fault current and isolates the faulty segments, from the remaining functional DC system, avoiding a grid-wide voltage collapse. Therefore with the presence of such DC/DC converters, the system component ratings are reduced and high-performance DC CBs may not be necessary. Instead, a DC disconnector (or standard AC CB) can be used for the purpose of permanent fault isolation or routine maintenance.

DC/DC converters can also connect DC systems of different voltage levels and with different DC technologies. This is of particularly interest in the circumstance of lack of standardizations at the beginning of HVDC grid application. DC/DC converters might become crucial elements to facilitate a meshed DC grid of different voltage levels tailored to local demands, and with flexibility for future expansion. The downside of the DC/DC converters is they have approximately 180%-200% VSC converter costs which imply that the number of converters and their location should be critically evaluated [11].

The conventional point to point HVDC topology has N-0 redundancy with lowest transmission reliability. A high reliability is achieved through redundancy of parts in the traditional power system, where N-1 and N-2 are generally accepted for the interconnected transmission systems [12][13]. In the presented test system, N-1 redundancy is desired for the transmission part of the subsea DC grid, In the event of a fault, on DC cable or converter, the fault will be isolated without affecting the normal operation of the remainder of the system. Nevertheless, the development of meshed DC grids with DC/DC converters has not been studied yet.

In this paper, a 200MW subsea DC collection grid is studied, as shown in Figure 1, which consists of two renewable energy sources (tidal stream and wind) and DC collection/transmission grids. The goal is to develop N-1 secure DC system with good connectivity and flexible expansion. Section II describes the 200MW subsea DC grid for collecting renewable energies from the sea. Section III focuses on the grid control and protection schemes and section IV on its modeling in Matlab/Simulink, and the simulation results to demonstrate the functionality of this DC grid under small signal disturbances and fault conditions are presented in section V.

# SUBSEA DC COLLECTION GRID

The subsea DC grid consists of two branches, branch 1 for a 100MW wind energy farm and branch 2 for a 100MW tidal/wave energy farm with their specifications shown in Figure 1. The topology of LCL DC/DC converter is shown in Figure 2. The 100MW wind farm has 20 individual 5MW wind generators and the tidal array consists of 50 individual 2 MW tidal turbines. The local farm–level collector systems are assumed to be of star/radial topology for simplicity and economic reasons, while the ring or meshed topology can also be used for increased reliability.

The two DC collection systems are assumed built at different stages with different local DC voltages, i.e. a 60kV substation for wind farm and a 40kV substation for wave / tidal stream farm. Each branch connects to an onshore 200MW VSC station using 250kV cable in a radial scheme. The onshore station has higher capacity in order to receive full power from the offshore system in case that one station/cable is at fault. A 40kV/60kV DC/DC converter and a DC intertie are installed to enable power exchange between the two branches. The insertion of this intertie DC/DC converter enables a grid-level loop transmission topology offering N-1 transmission redundancy.

The intertie DC/DC converter is located at the low voltage side substation (40kV) facilitating a power exchange between the two branches at a higher voltage (60kV) to reduce the loss. At the high voltage end substation a fast disconnector or a common AC Circuit breaker is used for the permanent isolation of intertie faults.

With the topology presented in Figure 1, a single DC fault at any point in this transmission loop will not affect the power transfer capability of the whole grid. If there is DC fault on one of the 250kVdc transmission lines, the faulty transmission line will be isolated by the AC side circuit breaker and the corresponding 200MW transmission DC/DC converter. In these circumstances, the transmission 200MW DC/DC converter naturally restricts the power and current feed into the faulty lines, consequently the voltage on local congregation bus will increase, because of the continued power infeed from plant. The design solution includes the droop control on the intertie 40kV/60kV/100MW DC/DC converter which will respond by redirecting the excess power from the faulty branch to the other branch. The above processes can be achieved in seamless manner and with no power interruption.

If there is a fault on 60kV DC transmission intertie, the intertie DC/DC converter will limit the fault current infeed from branch 2 40kV system and prevent fault propagation. The fault current infeed from branch 1 into 60kV system is limited close to zero by the wind farm 6.5kV/60kV DC/DC converters and the transmission DC/DC converter. The DC CB on the end of DC intertie is mechanical design with small current rating (or fast disconnector) and enables permanent cable isolation. Once the fault is isolated the power transfer can resume through both 250kV DC cables.

In practice, this grid may also be used to exchange power between onshore AC station 1 and AC station 2 through subsea corridors during low renewable energy power.

# System control and protection

The subsea DC grid integrates energy plants from resources of wind and tidal/wave current. Consequently the DC grid experiences a load profile characterized with fluid energy, which depends on the fluid speed. The variable speed energy conversion systems extract the maximum power by appropriate tracking control. The power extracted from wind or tide/wave is collected in the local substation and boosted up to 250kVdc for long distance transmission through multiple paths to onshore VSC converters.

## Renewable Plant and DC/DC Control Coordination

When the fluid speed is lower than the rated value, the main goal of the renewable plant control system is to get the maximum input power. The wind generator in the presented platform uses the concept of DFIG (Doubly Fed Induction Generator) however to reduce the platform complexity the DFIG wind energy conversion system is modeled as a current source regulated by active rectifiers.

The  tidal energy generators use PMSG (permanent magnet synchronous generator) concept and their AC voltages are diode rectified to give a dc output between 2kVdc-4kVdc as the tidal/wave speed is varying between 2m/s-4m/s. The maximum power tracking is implemented by local DC/DC converter E.

With synchronous generators, assuming that the voltage drop caused by current through synchronous reactance can be ignored, then the rectified voltage Urec is proportional to generator rotational speed ω. Under this condition, if one power point on the maximum power curve is known, then the other power points on the maximum power curve can be calculated [14]. This relationship can also be described using rectified voltage and torque, as follows:

(1)

where Tref is the torque command/reference, urec is the real time rectified voltage, and T1 is the torque corresponding to a rectified voltage u1 at maximum power tracking status. The actual torque on the shaft Tacu can be estimated by measuring power Pm and speed: by Tacu=Pm/ω.

The AC/DC converters 1&3 work in constant DC voltage control mode. They maintain the transmission line voltage at 250kVdc and regulate the AC side q-channel outputs such as reactive power in line with Grid Code requirements. In the test system, the reference of the reactive power is set to be zero.

All the DC/DC converters assume LCL topology which is based on two AC/DC IGBT-based and an internal LCL circuit [9][10]. The control strategy is discussed in [15]. Three reference frames can be utilized for decoupling the active and reactive power as shown in Figure 3. The frame dq represents a frame aligned with the capacitor voltage uc, and P1Q1 and P2Q2 are two coordinate frames at AC/DC ports 1 and 2 from Figure 2, positioned at u1ac and u2ac. φidq and φiPQ represent phases of uiac and iiac in frames dq and PiQi respectively, and Mid, Miq are control indexes, where i=1,2.

Some essential relations for decoupling the active power and reactive power are shown in equations (2)-(6).

(2)

(3)

(4)

(5)

(6)

where I1d and I2d are the d components of converter currents i1ac and i2ac in the dq frame, M1 and M2 are the modulation indexes for port 1 and 2 control respectively, U1acm and U2acm are rms values of u1ac and u2ac respectively, I1Q and I2Q are Q components of the converter currents in P1Q1 and P2Q2 frames respectively, Kc is a system constant, and Ucq is the q component of capacitor voltage uc in the dq frame.

Equations (2)-(6) show the active power and reactive power in the two ports of the DC/DC converter can be regulated by I1acd and I2acd in the dq frame, and I1Q and I2Q in P1Q1 and P2Q2 frames. Particularly equation (6) implies that Ucq is an indicator for power balance of the DC-DC converter. By maintaining Ucq to zero, power balance of the two terminals is ensured. To improve the dynamic response, a feed forward of Ucq is also used in the control of power (voltage or torque) terminal.

As shown in Figure 4, converters A, B and D work in voltage control mode and employ same control blocks. In normal operation they function to maintain the low voltage terminal DC voltage to be constant, Converter E enables maximum power tracking of the tidal energy generator which is in torque control mode. The intertie DC/DC Converter C works in power mode combined with voltage droop feedback from both DC voltages, for improved system stability. If there is disturbance in one branch, the energy in the other branch can be used to stabilize the troubled system.

## Converter DJ-Index Clamping

In the event of DC faults, the DC/DC converter limits the dc fault current naturally to close to rated level [10]. However it is desired to halt the feed-in converter current from the healthy terminal into the faulty circuit as to enable opening a disconnector or AC CB at very low current. The DC/DC converter fault current can be reduced by manipulating the modulation index M. As shown in Figure 4, all the control indices (M1d, M1q, M2d, M2q) are modulated by the proposed DJ-Index Clamping scheme.

This scheme provides a converter modulation index control in a square wave manner, as shown in Figure 5. All DC/DC converters use this modulation for DC faults in order to reduce fault current infeed and to attempt recovery after fault isolation. Two approaches can be utilized, namely “Droop-approach” and “Zero-approach”. In Figure 5, ① indicates the Droop- approach and ② is Zero-approach.

Droop-approach manages the modulation index reference clamping with a droop control manner. In normal operation the DC link voltages are in the safe zone as defined in Figure 5. When one of the normalized dc link voltages of two converter terminals is between D=0.2pu and Z=0.85pu (which is a DC fault situation), the clamping reference Mff is proportional to the DC link voltage, and when the dc link voltage is less than 0.2 pu, Mff is brought to zero. An alternative approach is Zero-approach, Mff flip flops to 0 immediately when a DC fault is detected. Droop-approach favors a DC grid where large power variation can be expected and zero-approach performs faster in a circuit with sluggish damping factor.

While DC current is reduced to zero the faulted cable will be isolated by DC disconnectors. The DC/DC converters have no information that isolation is completed, and therefore they will periodically attempt to increase modulation index in order to restore the power transfer. If Mff< Mth is detected for a time duration of Ts, the DC/DC converter is enabled for a period of Ts, and if during this period the DC voltage increases above a threshold Mth, the DC/DC converter will return back to normal operation (fault is isolated); otherwise the converter modulation indices are clamped to be zero (fault still present). The recovery cycle is repeated 2 times if the DC voltage does not recover. In the test system, Mth = 0.6 and Ts=25ms.

Furthermore, during normal operation if low DC voltage is detected for 100ms at either side of the DC/DC converter then the DC/DC converter will be permanently tripped. This control logic is represented by “Block” signal in Figure 5, where U1dcnom and U2dcnom are the nominal DC voltages at two converter terminals.

# System Average Value modeling

This section introduces the average value modeling of subsea DC grid components, including VSC converters, DC/DC converters and the renewable energy sources. The switching of power electronics will require significant computing time if detailed modes are to be used in the test system. To achieve acceptable performance in terms of accuracy and speed, average-value models (AVM) are used which eliminates the significant computing burden from detailed power-electronic building blocks (PEBB) [16].

## Converter Models

Since there is no energy storage component in the circuit, in the AVM VSC model the voltage and current on the ac side and dc side of are related by algebraic relations, as shown by equations (7)-(10). This model avoids topological changes which are required if switches are employed in the VSC model.

(7)

(8)

(9)

(10)

where Udc is the dc link voltage; M is the modulation index;

The DC/DC converter is modeled by Simulink nonlinear state space model directly in dq rotating frame [17]. The interface between AC and DC is expressed as [17]:

(11)

where i=1,2, for port 1 and 2 respectively.

## Offshore Energy Park Model

The platform shown in Figure 1 with 20 or 50 renewable energy extraction units will be difficult to be simulated due to significant computing time. In this study they are represented as two single equivalent 100MW generators [18], subsequently converters B and E are also modeled 100MW DC/DC units.

The wind and tidal mechanical sources are modeled based on Betz theory with corresponding fluid densities (1.024 Kg/m³ for air and 1025Kg/m³ for water). The 100MW variable speed wind generator is of DFIG type and outputs electrical power between 21.6MW and 100MW as the wind speed varies between 6m/s -10m/s.

In terms of tidal energy farm, a single 100MW PMSG Simulink model is used to represent 50 tidal generation units of 2 MW. The turbine outputs electrical power between 12.5MW and 100MW as the tidal stream speed changes between 2m/s-4m/s [19]. A diode rectifier is used with the rectified DC voltage varying between 2kV-4kV.

The DC/DC converters are designed as presented in [9].

# Simulation results

The subsea DC grid test system is built with Matlab/Simulink. Under normal operation, the two branches in the subsea grid extract powers from offshore plants and transmit to onshore stations. The intertie DC-DC converter transfers power as requested by the dispatcher in the range -100MW to +100MW. System response to small signal disturbances is studied then followed by two DC faults. The fault locations are shown in Figure 1. The DC faults are tested with a wind speed of 8m/s (half the rated power, i.e. 50MW) and tidal stream speed of 4m/s (full power i.e. 100MW) At the moment when the fault occurs, the intertie DC/DC converter C is dispatching about 0.15 pu tidal power from branch 2 into branch 1.

## Small Signal Response

As shown in Figure 6 (a), in branch 1, the wind speed changes in steps from 6m/s to 8m/s and then to 10m/s at a time interval of 1 second, then back to 8m/s at 3s. In the branch 2, the tidal speed changes in  steps  from 2m/s to 3m/s and then to 4m/s at an interval of 1 second, and back to 3m/s at 3s, as shown in Figure 6 (b). Before 4s, there is no power dispatching order on DC intertie converter C, and at 4s, the grid operator issues a 0.2pu power dispatchment from branch 2 to branch 1. All the labels and measurement points are given in Figure 1.

The responses of each converter confirm the stability of the test system and the ability to track renewable power changes. In Figure 6 (c), (d), (i) and (j), it is seen that controllers keep regulated variables at reference values, in particular the DC voltages are maintained at 60kV and 40kV bus. The diode rectified DC voltage Udcrec is proportional to the tidal speed, while the DC link voltage Udcvsc of active rectifier is maintained constant by the constant voltage control of DC/DC converter B, as shown in Figure 6 (g) and (h) respectively. Also the reactive power control loops operate normally for wide range of power orders, as shown in Figure 6 (e) and (f).

The intertie DC-DC converter transfers power as requested by dispatcher, and independently of the powers in the branches. After 4s, DC intertie converter C dispatches required power as indicated by PC1 and PC2. Consequently there is power drop on PD2 and Pac2, and more power delivered through PA2 and Pac1, as shown in Figure 6 (c) and (d). This DC/DC converter can also be set to operate in other control modes, like DC voltage control.

## DC Fault 1

Figure 7 shows the system responses for a branch 1 transmission cable DC fault at 2.5s. The local DC/DC converters limit the fault current and prevent fault propagation. The faulted 250kVdc transmission line is permanently isolated by opening AC CB1 and blocking transmission DC/DC converter A (100ms after the low DC voltage is detected, as introduced in section III). Both wind and tidal energy farm operate normally during after the fault, and full power is still delivered using the intertie branch after the faulted cable is isolated. The DC/DC converter C responds to DC voltage increase and increases power transfer resulting in re-dispatch of branch 1 power (50MW) to branch 2. There will be no DC voltage collapse on 60kV (or 40kV) DC cable.

## DC Fault 2

DC fault 2 is a pole to pole short circuit fault at 2.5s on interconnecting cable a-c, and Figure 8 shows the system responses. During the fault, DC/DC converters A, B and C initially limit the current and then reduce current to zero according to control in Figure 5. Within 10ms after the DC fault is detected, DC/CB is open and the fault is permanently isolated. The DJ indices of DC/DC converters A and B increase after 25ms, and since fault is cleared, they automatically resume normal operation. This process is completed within 50ms before the tripping time of DC/DC converters. The DC/DC C also uses DJ index clamping control, but it sees a permanent fault and it is tripped after 100ms. In this case, branch 1 recovers from DC fault 2 and full wind power is transferred but VSC1 power slightly reduces to compensate for the loss of intertie power. Tidal energy farm operate normally during after the fault and branch 2 remains full functionality. Since DCCB is open and DC/DC converter C is tripped, the tidal power is fully transmitted to onshore utility 2 through branch 2 and VSC slightly increases power transfer.

The details of DCCB opening process and converter resuming process are illustrated in Figure 9. UDCF2 is the local voltage which drops from 60kV to zero at 2.5s due to short circuit fault. The current through DCCB IDCCB is zero after opening DCCB; DC/DC converters A and B begin to resume after DCCB opening and the power delivery is recovered within 50ms. This is indicated by IB (current out of DC/DC converter B) and IA1 (into DC/DC A).

In this test, during the fault conditions a chopper with resistor is used to maintain the local 6.5kV dc voltage constant, which is a common practice with wind farms.

# Conclusion

A subsea DC collection and transmission grid with high power security is presented. By virtue of the applied LCL DC/DC converters, the electric power within the DC grid is collected locally at an intermediate voltage level and delivered at a transmission level while fault currents are limited. With the proposed DJ-Index Clamping control, DC/DC converters can reduce fault current to zero and they can recover when DC fault is isolated by other DC switchgear. It is demonstrated that interties between DC lines can be built by using a DC/DC converter and mechanical DC switchgear. The DC/DC converter in the intertie can be made to respond to DC voltage at either of the two DC lines and in this way it can rapidly re-dispatch power in case of DC faults. Two-branch system is shown in this article but expansion to multiple branches is possible in the future. The simulation results confirm small signal stability and responses for two representative DC faults.

Acknowledgements

This work was supported by the Engineering and Physical Sciences Research Council [grant number EP/K006428/1]; and the European Regional Development Fund [grant number LUPS/ERDF/2010/4/1/0164].

List of Symbols

Subscript

j=1,2                                port 1,2 of DC/DC converter

k=1,2,3,4,5,6,7,8             IGBT switches in DC/DC converters

Symbol

Cdj                         DC link capacitance at port j of DC/DC converter (F)

IA1                          current at port 1 of DC/DC converter A (A)

IB                           current at port 2 of DC/DC converter B (A)

ica, icb, icc               phase current in AVM model of AC/DC converter 1,3 (A)

IDCCB                        current through DC circuit breaker (A)

Ijd                           d component of DC/DC converter currents ijac (A)

Ijdref                        reference of d component of DC/DC converter currents ijac (A)

IjP                          P component of converter current at port j in PjQj frame (A)

Ijq                           q component of DC/DC converter currents ijac (A)

IjQ                         Q component of converter current at port j in PjQj frame (A)

IjQref                       reference of Q component current at port j in PjQj frame (A)

Kc                         system constant

Lj                          inductance at port j of DC/DC converter (H)

M                          modulation index of AVM model of AC/DC converter

Mff                        clamping reference of modulation index in the DJ-Index scheme

MDJ                         control index in the DJ-Index protection scheme

Mj                         modulation index for port j

Mjd                       d component of modulation index for port j

Mjq                       q component of modulation index for port j

Mth                        threshold of modulation index in the DJ-Index protection scheme

Pac1                       active power in AC station 1 (W)

Pac2                       active power in AC station 2 (W)

PAj                        active power at port j of DC/DC converter A (W)

PB                         active power at port 2 of DC/DC converter B (W)

PCj                        active power at port j of DC/DC converter C (W)

PDj                        active power at port j of DC/DC converter D (W)

PE                         active power at port 2 of DC/DC converter E (W)

Pj                          active power in port j of DC/DC converter (W)

Pm                         mechanical power of wind turbine (W)

Prec                       active power from AC/DC converter 2 (W)

Ptidal                      tide power from tidal energy farm (W)

Pvsc                       active power from AC/DC converter 4 (W)

Pwind                     active wind power from wind energy farm (W)

Qac1                      reactive power in AC station 1 (var)

Qac2                      reactive power in AC station 2 (var)

Rjdc                       resistance at port j (Ω)

Sk                         IGBT switches in DC/DC converter

Tacu                      the actual torque on the shaft (N∙M)

Tref                       torque command reference (N∙M)

Ts                         period in DJ-Index protection scheme (ms)

T1                         the torque of turbine shaft (N∙M)

uc                          capacitor voltage of DC/DC converter (V)

uca, ucb, ucc            phase voltage in AVM model of AC/DC converter 1,3 (V)

Ucd                        d component of capacitor voltage in the dq frame (V)

Ucq                        q component of capacitor voltage in the dq frame (V)

Ucqref                     reference of q component of capacitor voltage in the dq frame (V)

Udc                        DC link voltage of AVM model of AC/DC converter 1,3 (V)

UdcAj                                DC link voltage at port j of DC/DC converter A (V)

UdcB                                  DC link voltage at port 2 of DC/DC converter B (V)

UdcE                                  DC link voltage at port 2 of DC/DC converter E (V)

UdcC                                  DC link voltage at port 2 of DC/DC converter C (V)

UdcDj                                 DC link voltage at port j of DC/DC converter D (V)

UDCF2                               DC link voltage at fault point 2 (V)

Udcrec                                DC link voltage of converter AC/DC 4 (V)

UdcU1                                DC link voltage of converter AC/DC 1 (V)

UdcU2                                DC link voltage of converter AC/DC 3 (V)

Udcvsc                                DC link voltage of converter AC/DC 2 (V)

uj                            rectified voltage at maximum wind power tracking status (V)

ujac                         output voltage of port j (V)

Ujacm                      rms voltage of ujac at port j (V)

Ujdc                        DC link voltage at port j of DC/DC converter (V)

Ujdcnom                    nominal DC voltage at converter port j (V)

Ujpu                        per unit value of DC link voltage at port j of DC/DC converter C

urec                         the real time rectified voltage (V)

Vtide                       tide speed (m/s)

Vwind                      wind speed (m/s)

U1dcref                     reference of DC link voltage at port 1 of DC/DC converter A, B, D

αj                            phase angle between dq frame and PjQj frame (rad)

φjdq                         phase of ijac in the dq frame (rad)

φjPQ                        phase of ijac in the PjQj frame (rad)

ω                            rotational speed of turbine shaft (rad/s)

θ                             phase of capacitor voltage uc of DC/DC converter (rad)

dq frame            synchronous frame positioned at capacitor voltage uc of DC/DC converter

PjQj frame         synchronous frame positioned at AC voltage of port j of DC/DC converter

References

- CIGRE Working Group B4.52. HVDC grid feasibility study; CIGRE brochure 533, 2013.

- Zeng XJ, Zhang X, Chen F, Yang YB, Xu Yang. A four-leg three-level neutral-point-clamped inverter for offshore wind turbine with VSC-based HVDC transmission. International Transactions on Electrical Energy Systems 2015; 25, issue 1: 17–37. DOI: 10.1002/etep.1816

- Lu S, El-sharkawi MA. NEPTUNE power system: detection and location of switch malfunctions and high impedance faults, Proc. 2006 IEEE International Symposium on Industrial Electronics; 3; 1960-1965. DOI: 10.1109/ISIE.2006.295873

- Kawaguchi K, Kaneda Y, Araki E. The DONET: a real-time seafloor research infrastructure for the precise earthquake and tsunami monitoring. Proc. 2008 OCEANS MTS/IEEE Kobe Techno-Ocean; 1-4. DOI: 10.1109/OCEANSKOBE.2008.4530918

- Sanjari MJ, Alizadeh MO, Gharehpetian GB. Assessing the risk of blackout in the power system including HVDC and FACTS devices. International Transactions on Electrical Energy Systems 2013; 23, issue 1: 109–121. DOI: 10.1002/etep.1619

- Madureira AG, Pereira JC, Gil NJ, Peças Lopes JA, Korres GN, Hatziargyriou ND. Advanced control and management functionalities for multi-microgrids. International Transactions on Electrical Energy Systems 2011; 21, issue 2: 1159–1177. DOI: 10.1002/etep. 407

- Jovcic D, Hertem DV, Linden K, Taisne JP, Grieshaber W. Feasibility of DC transmission networks. Proc. 2011 2nd IEEE PES Innovative Smart Grid Technologies Conf.; 1-8. DOI: 10.1109/ISGTEurope.2011.6162829

- Khan J, Leon D, Moshhref A, Arabi S, Bhuyan G. Network security assessments for integrating large-scale tidal current and ocean wave resources into future electrical grids; Proc. IEEE; 101, issue 4: 956-977. DOI: 10.1109/JPROC.2013.2238491

- Jovcic D, Zhang L, LCL DC/DC converter for DC grids, IEEE Transaction on Power Delivery 2013; 28, issue 4: 2071-2079; DOI: 10.1109/TPWRD.2013.2272834

- Hajian M, Jovcic D, 30kW, 200V/900V LCL IGBT DC/DC converter prototype design and testing, Proc. 2014 IEEE Power and Energy Society Innovative Smart Grid Technologies; 1-5. DOI: 10.1109/ISGTEurope.2014.7028759

- Taherbaneh M, Jovcic D, Taisne JP, Nguefen S. DC fault performance and cost analysis of DC grids for connecting multiple offshore wind farms, Proc. 2013 IEEE Grenoble PowerTech; 1-6. DOI: 10.1109/PTC.2013.6652292

- Schneider K, Liu C.-C, McGinnis T, Howe B, Kirkham H. Real-time control and protection of the MEPTUNE power system, Proc. 2002 OCEANS MTS/IEEE Techno-Ocean; 3: 1799-1805. DOI: 10.1109/OCEANS.2002.1191906

- Latorres HF, Modeling and control of VSC-HVDC transmissions, Doctoral Thesis 2011, Royal Institute of Technology, School of Engineering, Electric Power System, Stockholm, Sweden.19-20

- Zhang HB, Fletcher JE, Greeves N, Finney SJ, Williams BW. One-power-point operation of variable speed wind/tidal stream turbines with synchronous generators. IET Renewable Power Generation 2011; 5, issue 1: 99-108. DOI: 10.1049/iet-rpg.2009.0207

- Lin WX, Jovcic D, Control strategy for a 2-terminal high power LCL DC-DC converter, Proc. 2013 IEEE Power and Energy Society General Meeting; 1-5. DOI: 10.1109/PESMG.2013.6672677

- Chiniforoosh S, Jatskevich J, Yazdani A., Sood V., Dinavahi V., Martinez JA, Ramirez A. Definitions and applications of dynamic average models for analysis of power systems. IEEE Transaction on Power Delivery 2010; 25, issue 4: 2655-2669. DOI: 10.1109/TPWRD.2010.2043859

- Lin WX, Jovcic D. High-Power High-Frequency converter modeling using Dommel’s and Runge Kutta methods in ABC and DQ Frame. Proc. 2014 IEEE Power and Energy Society General Meeting. 1-5. DOI: 10.1109/PESGM.2014.6939328

- Lin WX, Wen J Y, Liang J, Cheng S J, Yao MQ, Li NH, A three–terminal HVDC system to bundle wind farms with conventional power plants, IEEE Transactions on Power System 2013. 28, issue 3: 2292-2300. DOI: 10.1109/TPWRS.2012.2228506

- Green Rhino Energy. Tidal Stream Energy, online access: http://www.greenrhinoenergy.com/renewable/marine/tidal_stream.php. 17 September 2015.